
Fire Alarm Control Panel 2 Zones
User & Installation Manual
[image: image1.png]B g PR OIS T AT

] e ® D
Z1 Fire Z2Fire SoundAlarm AC Fault

@ ® ® ®
Z1Fault  Z2Fault SoundFault Bat.Fault

Evacuate Silence Test/Reset





IMPORTANT
This manual should be left with the panel after installation.

We reserve the right to change product specifications without prior notice. Copyright ©  Products 2017-Ver2.0
Contents

2Contents


31. Introduction


31.1  Product Features


31.2  Electrical Specifications


41.3  Fire Alarm System Limitations


51.4  Installation Precautions


52.Control Panel Installation


52.1   Important Notice


62.2   Mounting The Enclosure


62.3   Power Connection


72.4   Battery Installation


72.5   Terminals For Connection


82.5.1  Zones Installation


82.5.2  Relay Outputs


82.5.3  NAC Output Circuit Installation


82.5.4  DC24V Supply


82.5.5  RS485 Communication


3. Control panel fascia
9
4.Panel Operation
9


1. Introduction                                                     

The 2 zones panel is designed to meet the requirements of EN54 Parts 2 & 4.

The fire alarm control panels （2 Zones) provide all of the sophisticated features required of a leading edge conventional fire alarm system along with the simple operation and efficient installation methods demanded by both installers and building users. 
A comprehensive range of auxiliary devices is available to operate with the fire control panels including optical, ionization, photoelectric, photoelectric-thermal and heat detectors. 

Each of the system components has been specifically designed to operate as part of the system. This provides assurance that the control panel, smoke detectors, interface devices and the ancillary components are all fully compatible with one another and that the full range of system functionality is supported by each device.

Product Features

The panels have the following key features:

2 conventional input zones.

1 notification appliance circuits (NAC) with built-in synchronization for ANSI 3.41and Gentex.

The panel comes with a 2 amp power supply.  

Dedicated alarm and trouble relays.
1 RS485 can be able to connect the other panel.

Housed in a 205mm W x 258mm H x 81mm D metal enclosure.

Enclosure supports two 12V, 4Ah backup batteries.
The panel can be used independently or connect by RS485.

[image: image2.png]® ® ® ®
Z1 Fire Z2Fire  SoundAlarm AC Fault
® ® ® ®
Z1Fault  Z2Fault SoundFault Bat.Fault

Evacuate Silence Test/Reset





Electrical Specifications

	Primary AC
	120VAC 50/60 Hz  Power supply rating

	
	240VAC 50/60 Hz  

	Power supply rating
	2 Amps @ 24VDC  

	Maximum Battery Charging Current
	0.98 Amps @ 26VDC 

	Initiating Device Circuits 2 Zones
	Alarm Zone 2

	Normal Initiating Operating Voltage
	23VDC, Maximum 26VDC, regulated

	Normal Quiescent Current (normal status)
	<50mA

	Alarm Current (not include the others)
	<150 mA

	Short Circuit Initiating Current (per zone)
	35mA Maximum

	Maximum Initiating Resistance (per zone)
	10 ohms

	Initiating End-of-Line Resistor
	4K7 ohms, 1/2W  5%

	Standby Detector Current (per zone)
	4mA maximum

	Maximum Detector Count (per zone)
	30 detectors

	Initiating Cabling Type
	18AWG Twisted Shielded pair (14 – 18 AWG)

	Detector Base Impedance
	430 ohms

	Notification Appliance Circuits
	1 NACs, Special Application

	Maximum NAC Current Rating 
	1 Amp maximum per circuit

	NAC Operating Voltage
	26VDC Nominal, 30VDC Maximum

	NAC End-of-line Resistor
	1N4007 Diode 

	FAULT Relay rating
	2A & 30VAC, resistive

	Alarm( Auxiliary ) Relay rating 
	2A & 30VAC, resistive


Fire Alarm System Limitations

An automatic fire alarm system – in general is made up of smoke, heat & other detectors, manual call points, audible warning devices, fire alarm control panels with remote notification capability, which can supply early warning of a developing fire. Such a system, on the other hand, is unable to assure protection against property damage or loss of life resulting from a fire.

The manufacturer recommends that smoke and/or heat detectors must be positioned throughout a protected premise following the recommendations of the current edition of the EN Standard, manufacturer’s recommendations contained in the Guide for proper Use of System Smoke Detectors, which is made available at no charge to all installing dealers. A study by the Federal Emergency Management Agency (an agency of the United Europe) indicated that smoke detectors may not go off in as many as 35% of all fires. A fire alarm system may not provide timely or sufficient notice, or might not function, for a diversity of reasons:

Smoke detectors may not sense fire where smoke cannot reach the detectors such as in chimneys, in or behind walls, on roofs, or on the other side of closed doors. Smoke detectors also may not sense a fire on another level or floor of a building. A second-floor detector, for example, may not sense a first-floor or basement fire.

Particles or combustion or “smoke” from a developing fire may not reach the sensing chambers of smoke detectors because:

Barriers such as closed or partially closed doors, walls, or chimneys may inhibit particle or smoke flow.

Smoke particles may become “cold,” stratify, and not reach the ceiling or upper walls where detectors are located.

Smoke particles may be blown away from detectors by air outlets.

Smoke particles may be drawn into air returns before reaching the detector.

The amount of “smoke” present may be insufficient to alarm the smoke detectors. Smoke detectors are designed to alarm at various levels of smoke density. If such density levels are not created by a developing fire at the location of detectors, the detectors will not go into alarm. Smoke detectors, even when working properly, have sensing limitations. Detectors that have photo electronic sensing chambers tend to detect smoldering fires better than flaming fires, which have little visible smoke. Detectors that have ionizing-type sensing chambers tend to detect fast-flaming fires better than smoldering fires. Because fires develop in different ways and are often unpredictable in their growth, both types of detectors are necessarily best and a given type of detector may not provide adequate warning of a fire. A smoke detector cannot be expected to provide adequate warning of fires caused by arson, children playing with matches (especially in bedrooms), smoking in bed, and violent explosions (caused by escaping gas, improper storage of flammable materials, etc.).  Heat detectors do not sense particles or combustion and alarm only when heat on their sensors increases at a preset rate or reaches a predetermined level. Rate-of-rise heat detectors may be subject to reduced sensitivity overtime. For this reason, the rate-of-rise feature of each detector should be tested at least once per year by a qualified fire protection expert. Heat detectors are designed to protect property, not life.

IMPORTANT! Smoke detectors must be installed in the same room as the control panel and in rooms used by the system for the connection of alarm transmission wiring, communications, signaling, and/or power. If detectors are not located near the control panel, a developing fire may damage the alarm system, crippling its ability to report a fire.

Audible warning devices such as bells may not alert people if these devices are located on the other side of closed or partly open doors or are located on another floor of a building. Any warning device may fail to alert people with a disability or those who have recently consumed drugs, alcohol or medication. Please note that:

Strobes can, under certain circumstances, cause seizures in people with conditions such as epilepsy.

Studies have shown that certain people, even when they hear a fire alarm signal, do not respond or comprehend the meaning of the signal. It is the property owner’s responsibility to conduct fire drills and other training exercise to make people aware of fire alarm signals and instruct them on the proper reaction to alarm signals.

In rare instances, the sounding of a warning device can cause temporary or permanent hearing loss.

A fire alarm system will not operate without any electrical power. If AC power fails, the system will operate from standby batteries only for a specified time and only if the batteries have been properly maintained and replaced regularly.

Equipment used in the system may not be technically compatible with the control. It is essential to use only equipment listed for service with your control panel.

Telephone lines needed to transmit alarm signals from a premise to a central monitoring station may be out of service or temporarily disabled. For added protection against telephone line failure, backup radio transmission systems are recommended.

The most common cause of fire alarm malfunction is insufficient maintenance. To keep the entire fire alarm system in excellent working order, ongoing maintenance is required as the manufacturer’s recommendations, and UL and NFPA 72 shall be followed. Environments with large amounts of dust, dirt or high air velocity require more frequent maintenance. A maintenance agreement should be arranged through the local manufacturer’s representative. Maintenance should be scheduled monthly or as required by National and/or local fire codes and should be performed by authorized professional fire alarm installers only. Adequate written records of all inspection should be kept.
Installation Precautions

WARNING – Several different sources of power can be connected to the fire alarm control panel. Disconnect all sources of power before servicing the control unit. Associated equipment may be damaged by removing and/or inserting cards, modules or interconnecting cables while the unit is energized.
Do not attempt to install, service, or operate this unit until this manual is read and understood fully.
CAUTION – System Reacceptance Testing Requirements. To ensure proper system operation, this product must be tested in accordance with NFPA 72 after any programming operation or change in site specific software. Re-acceptance testing is required after any change, addition or deletion of system components, or after any modification, repair or adjustment to system hardware or wiring.  All components, circuits, system operations, or software functions known to be affected by a change must be 100% tested. In addition, to ensure that other operations are not inadvertently affected, at least 10% of initiating devices that are not directly affected by the change, up to a maximum of 50 devices, must also be tested and proper system operation verified.
This system meets NFPA requirements for indoor dry operation at 0-49° C/32-120° F and at a relative humidity up to 93 ±2%RH (non-condensing) at 32 ±2° C/90 ±3° F. However, the useful life of the system's standby batteries and the electronic components may be adversely affected by extreme temperature ranges and humidity. Therefore, it is recommended that this system and all peripherals be installed in an environment with a nominal room temperature of 15-27°C/60-80° F.
Verify that wire sizes are adequate for all initiating and indicating device loops. Refer to the manual specifications section for maximum allowable I.R. drop from the specified device voltage.

Like all solid state electronic devices, this system may operate erratically or can be damaged when subjected to lightning induced transients. Although no system is completely immune from lightning transients and interferences, proper grounding will reduce susceptibility. Overhead or out-side aerial wiring is not recommended, due to an increased susceptibility to nearby lightning strikes. Consult with the Technical Services Department if any problems are anticipated or encountered.

Disconnect AC power and batteries prior to removing or inserting circuit boards. Failure to do so can damage circuits.
Remove all electronic assemblies prior to any drilling, filing, reaming, or punching of the enclosure. When possible, make all cable entries from the sides or rear. Before making modifications, verify that they will not interfere with battery, transformer, and printed circuit board location.
Do not tighten screw terminals more than 9 in-lbs. Over-tightening may damage threads, resulting in reduced terminal contact pressure and difficulty with screw terminal removal.


This system contains static-sensitive components.  Always ground yourself with a proper wrist strap before handling any circuits so that static charges are removed from the body. Use static-suppressive packaging to protect electronic assemblies removed from the unit.
Follow the instructions in the installation, operating, and programming manuals. These instructions must be followed to avoid damage to the control panel and associated equipment. FACP operation and reliability depend upon proper installation by authorized personnel.                                  

2.Control Panel Installation                                           

2.1   Important Notice 

This product should be installed, commissioned and maintained by suitably qualified service personnel with reference to IEE regulations and any statutory requirements, for use in fire alarm signaling systems, only when installed in accordance with this manual and the latest National Fire Protection Association Standards NFPA 72; the National Electrical Code (NFPA 70); the Life Safety Code (NFPA 101); and/or the local authority having jurisdiction (AHJ). It is possible to apply system components incorrectly or arrange system components and installation wiring so that required life safety functions are NOT performed. As a result, lives may be lost.

To minimize this possibility:

DO NOT deviate from any installation instructions contained in this manual.

DO NOT assume any installation details not shown in this manual.

DO NOT alter any mechanical or electrical features of the equipment supplied

BE FAMILIAR with the building code, fire prevention code, and/or requirements of the Authority Having Jurisdiction (AHJ) in the locale of the installation.
! Caution !

Under normal and fault conditions, AC line voltages may be present on any terminal. Touching any component could be hazardous and result in loss of life. A short circuit can result in arcing that could cause molten metal injuries to testing personal. To minimize this possibility, only qualified electrical technicians familiar with electrical hazards should perform these checkout procedures. Safety glasses should be worn by such personnel, and instruments used for voltage measurement should be designed for the purpose and should be in good mechanical and working order.
2.2   Mounting The Enclosure
Install the enclosure as follows:

Carefully unpack the system components and inspect for any damage due to shipping.

Mount the enclosure in a clean, dry, vibration-free area where extreme temperatures are not encountered. The location should be readily accessible with sufficient room for easy installation and maintenance.

Mount the cabinet by using the two mounting holes located in the upper back of the cabinet. After the panel has been properly located using the mounting holes, the panel can be secured.

Complete all conduit connections to the cabinet. Use the knockouts provided in the top and the sides.

Wire must NOT enter the bottom of the cabinet, since this area is intended for batteries only.
Before proceeding with the installation, please read the section Panel Operation.

Installation of the panel should be carried out by qualified personnel.

Using the metal box as a template, mark the position of the fixing holes on the wall.  Drill and plug the wall, then screw the panel to the wall.  Ensure the panel is free from knockout discs, swarf and other debris.

The back of panel box is as below, there are three wiring holes on the back, and another three holes on the top of box for cable wiring. And there are six diameter 8mm holes on the back of box for screws to fix the box on the wall.

[image: image3.png]



2.3   Power Connection
WARNING!

To reduce the risk of electrical shock, make sure that all power has been turned off or disconnected prior to attempting to connect AC power to the Power Supply.

Apply the AC Power BEFORE connecting the batteries to the Panel!

Provide the Fire Alarm Control Panel with a dedicated AC Circuit rated 10 Amps or higher. Refer to figure 2.1 for the AC power wiring diagram.

Enter the power cable into the Cabinet via a knock out hole.

Attach the brown (live) wire from the source to the terminal labeled “L” terminal.. 
Attach the blue (neutral) wire from the source to the terminal labeled “N” terminal. 
Attach the ground wire from the source to the terminal labeled “E” terminal.
[image: image4.png]=C

56

AC Power

L




[image: image5.png]Red iack



                             

2.4   Battery Installation

The batteries are placed at the bottom of the enclosure. The panel is fully protected if the batteries are connected in the wrong polarity. The yellow battery fault LED on the display circuit board will show steady in such a condition. When the green battery LED is on steady it shows that the battery condition and connections are normal.  

[image: image6.png]



[image: image7.png]



The panel is turned off , connect the battery without AC power then the panel will not working.

The panel are working in the normal if the AC power shut off then the battery will automatic supply power to panel. 
2.5 Terminals For Connection

[image: image8.png]



2.5.1 Zones Installation

The panel has either 2 class B conventional input zones. Wire the smoke, heat or multi detector positive terminals to the terminal labeled “+” and the negative detector terminals to the terminal labeled  “-“ as shown in below which shows the panel. Each active zone requires a 4K7end of line (EOL) resistor at the very end of the zone. 
[image: image9.png]



2.5.2 Relay Outputs

Each panel has 2 forms C relays, 1 common alarm and 1 common fault functions. All 2 relay outputs (Alarm and fault relays) carry the same voltage and current ratings. The relays are rated 2 amps at 30VDC.

[image: image10.png]ZONE1 | ZONE2





Fault Relay Output
If any fault occurs in the panel, the Fault Relay would be activated and output relay signal outputs(C, NO). 

Fire Relay Output
If any zones fire alarms, the Fire1 relay would be activated and output relay contacts(C, NO). Meanwhile, the Sound output would be activated.

2.5.3 NAC Output Circuit Installation

The control panel has 1 built-in output notification appliance circuits (NAC).

Output circuit 1 wired as a class B NAC output.  Observe the polarity of the wiring and the placement of the 1N4007 diode end of line (EOL) located at the very end of the class B wiring.  
[image: image11.png]


A end of line diode must be fitted at the end of the circuit. Motorised fire bells may be used, but solenoid bells MUST NOT be connected to the panel.

2.5.4 DC24V Supply
The panel provides a 24VDC/1amp supplies that one is a permanent 24VDC output.
[image: image12.png]



2.5.5 RS485 Communication

The RS485 can be able to connect the other panel or repeater.

[image: image13.png]Supervised
Power Limited

||





3. Control panel fascia                                             

In addition to the mandatory controls and indications required by the EN54-2/4 standards, Reset, Test, and Silence Alarm/Fault buttons are provided to allow easy operation to the control pane.

[image: image14.png]24VDC





4.Panel Operation                                                   

Normal Status.
If the panel is in its normal condition, the RUN led (above the TEST/RESET button) would flash once every 10 seconds (without communication) or 5 seconds (with communication)..
Performing a lamp test.
If the panel is in its normal condition, pressing the Test/Reset button will cause the panel to perform a lamp test. In the normal condition, press and hold down Test/Reset button about 10 seconds, the panel would be reset.

Resetting the panel after a fire or fault is detected.
To reset the panel after a fire or fault event, press the Silence button first and then press the Reset button.

Resetting the all the panels.
If any of the panel functions have been activated, pressing Silence button first and then press the Reset button will return the panel to its normal condition. 

Silencing the internal buzzer.
If a fault or a alarm is detected by the panel, the internal buzzer will sound. To silence the buzzer press the Silence button.
Silencing the Sound Alarms.
If a fire is detected, the panel will automatically activate the sound circuits. To silence the sound alarms, press and hold down the Silence button about 5 seconds.
Active sound alarm manually.
Anytime, press the Evacuate button, the sound output would be activated.
Fault Finding
RUN LED blinks intermittently
This is perfectly normal and indicates that the processor is running an internal memory check.

Fault LED and sense zone fault LED flashing, buzzer sounding.
Faults monitored are:

• Open circuit on the sense zone wiring.

• Detector head removal.

Check all detectors and call points on the sense zone indicated. Check wiring is as in example diagrams and ensure the end of line monitor is a 5k6 resistor or an active end of line device.

Sound fault LED flashing, buzzer sounding.
Faults monitored are:

• Open circuit on the sound output wiring.
• Short circuit on the sound output wiring.
• The end of line diode not connected or not connected correctly.
Head removal not working.
Check compatible base is being used and is wired correctly.

Other faults.
Switch off the power supply and restart the power on.

Fault Output
The fault output, marked FAULT on the PCB, is a set of volt free changeover contacts. When the panel is in fault, common (C) is shorted to normally open (NO).  In normal operation with no faults, common (C) is shorted to normally closed (NO).
202





111





254





AC to DC


Power Supply





27VDC Output





4AH Battery





4AH Battery





Red





Black





  ZONE1


  +   - 





  ZONE2


 +   - 





  FAULT


 C NO 





 FIRE


C NO 





  SOUND


 +   - 





  RS485


   A  B 





  24VDC


   +  - 





4K7 EOL





in + out+





in – out-





in – out-





in + out+





1N4007








- 3 -

[image: image15.png]


[image: image16.png]® @ ® ®
21 Fire Z2Fire  SoundAlarm AC Fault

® ® ® ®
Z1Fault  Z2Fault SoundFault Bat.Fault

® O

Evacuate Silence Test/Reset




